## Readme
Calculation sheet: |  | Figure: overall representation of the system design. The tool needs to 1. have a detailed list of appliances, then 2. it will design a system based on the products user has chosen. And finally, 3. a Bills of Quantities will be estimated. (Source: Victron)
Objective: Pre-design system and verify component adequacies
Key outcomes: | 1. Fast pre-design of the system
2. Budget estimation of the system
3. List of detailed components
4. Verify adequacy between the different components
Color code of the sheets:
Grey scale | Comments
Input | User must give a numerical value
Calculation | Automatic calculation
Output | Automatic calculation
Procedure:
1st: list in tab '1. Appliances' the ones that require backup and collect the following data:
- Name: | Short indicative name
- Model: | Indicated on the appliance
- Number of items: | example 10 Tube LED 40W
- Nominal power: | Usually indicated on the product
- Surge power: | Rarely indicated, can be find on internet based on the model Surge power is the peak demand power of the appliance (e.g. a printer requires an extra power at the beginning to heat the ink)
- Hours of use during day: | Ask users
- Hours of use during night: | Ask users |  | I./
We also advise to take a picture of each appliance with the brand name
2nd: design your system in '2. System'. Advanced options are available for each technology in tabs '2bis …'
Backup characteristic: | Characterise the backup required (hours of backup and lifetime)
Components choice: | Pick the inverter, panels & battery you want from existing lists (possibility to add new models to the lists
Recommended design: | Adjust the design to your need based on an automatic sizing
System adequacy: | Verify the adequacy between the different components (list of warnings)
If new componetnt must be added to the list, we advise to have the review of an expert.
3rd: BoQ is generated automatically with the products selected. The BoQ accounts for ligthning arrestor and electricity adaptation. User is free to adapt the BoQ based on the exact needs. Some information must be indicated manually (see the following)
Inverters | You can breakdown the inverter you want based on the power range and market availability
Electricity adaptation | Indicate the electrical adaptation required for the buildings (sockets, switches & lights).
Authorship & Licence
This tool was developed by:
Gauthier Limpens
This model has been designed for Uganda case stydt and for small hybrid (solar-utility) system (<25kW), where the utility is not realiable (autnomy represents shortage).
It was developed in a open-science spirit. The tool cannot be sold.
License:
The tool is under the Apache 2.0 License (available here : https://www.apache.org/licenses/LICENSE-2.0 )
Source:
This tool is inspired from the work of Victron & System Advisor Model (NREL (USA))

## 0. Info
General info
Country
City
Adress
Beneficiaries info
Beneficiairies
Description
Funding source
Financial info
Available budget

## 1. Appliances
Name | Quantity | Nominal power per unit | Surge power per unit | Nominal power | Surge power | Day use | Nigh use | Daily use | Fast design:
Units | [-] | Watts | Watts | Watts | Watts | Hours | Hours | Watt-hours | PV | 15.7393 | [kW]
Big lights LED | 23 | 36 | 36 | 828 | 828 | 4 | 6 | 8280 | Batteries | 35.472 | [kWh]
Outside lights LED | 2 | 36 | 36 | 72 | 72 | 2 | 12 | 1008 | Inverter | 2.4024 | [kW_out]
Baby incubators | 0 | 850 | 850 | 0 | 0 | 12 | 12 | 0
Phototherapy lamp | 1 | 150 | 150 | 150 | 150 | 12 | 12 | 3600
Oxygen concentrator | 3 | 560 | 560 | 1680 | 1680 | 12 | 12 | 40320
Watts: 0; Watts: 0 | 0
Watts: 0; Watts: 0 | 0
Watts: 0; Watts: 0 | 0
Watts: 0; Watts: 0 | 0
Watts: 0; Watts: 0 | 0
Watts: 0; Watts: 0 | 0
Watts: 0; Watts: 0 | 0
Watts: 0; Watts: 0 | 0
Watts: 0; Watts: 0 | 0
Watts: 0; Watts: 0 | 0
Watts: 0; Watts: 0 | 0
Watts: 0; Watts: 0 | 0
Watts: 0; Watts: 0 | 0
Watts: 0; Watts: 0 | 0
Watts: 0; Watts: 0 | 0
Units: Total :; Watts: 2730; Watts: 2730 | 53208
Simultaneous coefficient : |  | Simultaneous coefficient : |  | 80% | 80%
Account the probability that all appliances are used at the same time. (use 80% if no measurements)
|  |  | Total : | 2184 | 2184 | Watts
| Total nominal power : Estimate the nominal/averaged power that must deliver the inverter. |  |  |  |  | Surge total power : Some appliances can generate a peak of power at their start (i.e. high inductance), this peak is called the 'surge power' and sometimes indicated on the appliance. It is critical to ensure that the inverter can supply this peak of power, generally higher than the average output power of the inverter.
Database for common appliances
Automatic name: | Sector | Manufacturer | Model | Nominal power per unit | Surge power per unit | Comment
Light LED - big (office) | All | Light LED - big (office) |  | 36 | 36
Light LED - small (office) | All | Light LED - small (office) |  | 18 | 18
Light LED - big (outside) | All | Light LED - big (outside) |  | 36 | 36
Printer Epson LX-300-II 220V | ICT | Printer Epson LX-300-II 220V |  | 23 | 168
Scanner HP Scanjet G3010 | ICT | Scanner HP Scanjet G3010 |  | 21 | 35
Office computer | ICT | Office computer |  | 120 | 120
wifi box | ICT | wifi box |  | 10 | 10
Kanmed AB Babywarmer BW3 | Medical | Kanmed AB | Babywarmer BW3 | 100 | 100
Medpath OLV-10 | Medical | Medpath | OLV-10 | 550 | 550
Phoenix Medical Systems Phototherapy unit Brilliance pro | Medical | Phoenix Medical Systems | Phototherapy unit Brilliance pro | 25 | 25
Airsep Newlife | Medical | Airsep | Newlife | 350 | 400
Heal Force INFANT INCUBATOR YXK-6G | Medical | Heal Force | INFANT INCUBATOR YXK-6G | 450 | 450
Being BRW-3000B | Medical | Being | BRW-3000B | 1000 | 1000
CEPHIED GX - IV R2 | Medical | CEPHIED | GX - IV R2 | 336 | 400
Dison/Lotus BB-100 | Medical | Dison/Lotus | BB-100 | 650 | 650
SMAF YX930D | Medical | SMAF | YX930D | 250 | 250
Yuwell 7F-5 | Medical | Yuwell | 7F-5 | 500 | 500
Zybio Z3 | Medical | Zybio | Z3 | 200 | 200
Pima Alere CD4 | Medical | Pima Alere | CD4 | 63 | 63
Haier 4℃ Blood Bank Refrigerator | Medical | Haier | 4℃ Blood Bank Refrigerator | 250 | 350
Blood bank refrigerator XY-190 | Medical | Blood bank refrigerator | XY-190 | 200 | 300
EDAN X10 | Medical | EDAN | X10 | 168 | 168
Pima EID | Medical | Pima EID |  | 144 | 144
Sysmex | Medical | Sysmex |  | 788 | 788
DC 112F | Medical |  | DC 112F | 65 | 65
Hettich EBA200 | Medical | Hettich | EBA200 | 120 | 120
Olympus CX21FSI | Medical | Olympus | CX21FSI | 60 | 60
AEROplus AE5.00 | Medical | AEROplus | AE5.00 | 295 | 295
JIANGSU 8F-5A | Medical | JIANGSU | 8F-5A | 400 | 400
Famed lodz Solis 30FA | Medical | Famed lodz | Solis 30FA | 48 | 48
ADH BCD30-898 | Medical | ADH | BCD30-898 | 228 | 228
Dufex Ohmeda 9100C | Medical | Dufex Ohmeda | 9100C | 1000 | 1000
Longfian Jay-10 | Medical | Longfian | Jay-10 | 880 | 880
Famed lodz YDK-L01 | Medical | Famed lodz | YDK-L01 | 50 | 50 | Power not sure
Fazzini F-18.00 | Medical | Fazzini | F-18.00 | 85 | 85
Ningbo David medical HKN-90 | Medical | Ningbo David medical | HKN-90 | 120 | 120
Titanox | Medical | Titanox |  | 400 | 400
Hemocue HB301 | Medical | Hemocue | HB301 | 30 | 30 | Power not sure
CENCE TDZ5-WS | Medical | CENCE | TDZ5-WS | 400 | 400

## 2. System
System design | [5 empty] | Schematic representation of the system:
INPUT:
Backup characteristic
Time when backup must be available. It should be between 1 and 48 hours.
This is case specific and should be estimate with the user based on their needs.
Hours of autonomy | 8 | [hours]
Occurrence of shortage | 7 | [times per week]
Battery lifetime | 8 | [years]
Components choice (chose from the lists)
Panel type | risen RSM150-8-485M |  | New panel can be implemented in 'Panels' tab
Battery type | Rita DG12-200 |  | New battery can be implemented in 'Battery' tab
Hybrid Inverter type | Raggie RG-MH5500W Plus |  | New Hybrid inverter can be implemented in 'Hyb. Inverter' tab
DESIGN OUTPUT (results):
Recommended design (based on 1. Appliances & components chosen)
Inverter-demand-utility
recommended number | 3 | Inverter
User choice: | 3
Inverter-PV
Recommended number of pannel | 32.4168 | Panels
Recommended number of pannel per inverter | 11
Design per inverter, user choice: | 12
Max in series: | 9
In series | 6 |  | ok
In parallel | 2 |  | ok
Total panels for system | 36
Inverter-batteries
recommended number | 14.78 | Batteries
User choice | 16
recommended Voltage | 48 | Volts
System voltage | 48
in series | 4 | Batteries
in parallel | 4 |  | ok
Expected autonomy | 8.6604 | hours
Expected lifetime (at 25°C & respected DoD): | 4.2017 | Years
Check system adequacy:
address carefully the comments. Red is a design error, orange is a data comment.
Inverter-demand-utility |  |  | Inverter-panels |  | Inverter-batteries
|  |  | Vmin PV | 253.32 | Batt. Voltage system | 48
|  |  | Vmin Inverter | 109.0909 | Inv. Voltage system | 48
Comment | This tool is preferred for 1 inverter design. Consider using a more powerful inverter. Otherwise, use inverters in parallel (this requires good installation skills). |  | Vmin ok? | Ok | System voltage | Ok
|  |  | Voc PV | 302.1 | Power max batt | 4165.0648
|  |  | Vstart Inverter | 132 | Power max demand | 2184
DC coupling | High power system. Consider a AC-coupling system |  | Vstart ok? | Ok | System power | Ok
|  |  | Voc PV | 302.1 | Surge power batt | 7080.6101
|  |  | Vmax Inverter | 454.5455 | Surge power demand | 2184
|  |  | Vmax ok? | Ok | System surge power | Ok
|  |  | Imax PV | 23 | Max current batt | 21.693
|  |  | Imax inverter | 100 | Max current Inv | 100
|  |  | Imax ok? | Ok | System current check | Ok
|  |  | Pdc PV | 5826.36 | Cycle batt | 1500
|  |  | Pdc_in Inv | 50000 | Cycle expected | 2856
|  |  | Pmax ok? | Ok | Lifetime | Number of cycles insufficient to ensure correct lifetime. Advice: decrease Depth of Discharge, chose another battery
[5 empty] | Batt in parallel | 4
[5 empty] | Max batt in parallel | 3
[5 empty] | Battery in parallel | Too many batteries in parallel, consider using 2V batteries or increase system voltage
Comment: | 0 |  | Comment | 0 | Comment: | 0
48
48
Watts
Watts
Watts
Watts
Amps
Amps
Watt-hours
Watt-hours
hours
Note on A24: Gauthier Limpens: Good practice: maximise the number in series to increase system voltage and decrease Wiring losses (RI²)
Note on A33: Gauthier Limpens: Good practice: maximise the number in series to increase system voltage and decrease Wiring losses (RI²)
Note on H56: Gauthier Limpens: MARGE advise max 3 batteries in parallel. Indeed, the battery status will be lead by the worst one. Thus it is better to have a lower number of batteries in parallel.

## 2bis. Panels
Panels (advanced)
Input |  |  | Comments:
Daily demand | 53208 | [Watt-hours]
Mean irradiation | 5366 | [Watt-hours/day] | Data from Renewable ninja - https://www.renewables.ninja/
System efficiency (panel to user) | 70% | [-] | Advised to take around 65-75% (source : Victron training)
Panel efficiency (shadow, tilt,…) | 90% | [-] | Usually between 80% and 90% (source : Victron training)
Panels properties |  |  | Comments:
Power | 485.53 | [Watt] | Rated output power
Voltage (nominal) | 42.22 | [Volt] | Optimal output voltage
Current (nominal) | 11.5 | [Amper] | Optimal output current
Voltage (open circuit) | 50.35 | [Volt] | Open circuit voltage
Current (short circuit) | 12.25 | [Amper] | Short circuit current
Result |  |  | Comments:
Peak power required | 15739.311 | [Watt]
Number of panels advised | 32.4168 | [Panels]
Min panels in serie V based | 2 | [Panels] | Constrained by min voltage to start the controller
Max panels in serie V based (depends on controller) | 9 | [Panels] | Constrained by the max voltage that controller can allow
Max panels in parallel I based (depends on controller) | 8.1633 | [Panels] | Constrained by the max current that controller can allow
Database Solar panels |  |  |  |  | Database available in tool System Advisory Model 2021.12.2 https://sam.nrel.gov/
| Manufacturer | Type | Power | Vmpp | Impp | Voc | Isc | Datasheet | Comment
Victron Energy SPM20-12 | Victron Energy | SPM20-12 | 20.165 | 18.5 | 1.09 | 22.6 | 1.19 |  | Data from VE-MPPT-Calc-4_0
risen RSM144-410M | risen | RSM144-410M | 410.565 | 40.65 | 10.1 | 48.9 | 10.7 | risen_RSM144
FUTURASUN FU 310 P | FUTURASUN | FU 310 P | 310.527 | 37.1 | 8.37 | 45.7 | 8.85 | 2020_FuturaSun_72p_300-330W_en
risen RSM150-8-485M | risen | RSM150-8-485M | 485.53 | 42.22 | 11.5 | 50.35 | 12.25 | risen_RSM150

## 2bis. Batteries
Batteries (advanced)
Input |  |  | Comments | [11 empty] | Number of cycles for different Depth of Discharge (DoD)
Hours of autonomy | 8 | [hours] | Battery is sized to support x hours of autonomy
Average power | 2184 | [Watt] | Average power to be supplied
Daily use | 53208 | [Wh]
Battery type | Lead Acid Gel/VRLA | [-]
Depth of Discharge | 50% | [%] | Maximum capacity of battery used (for lead battery, this dictate the lifetime)
Charge current (advised) | 10% | [%/h] | Advised charge current. 10h means a charge in 10h
Charge current (max) | 20% | [%/h] | Advised discharge current. 10h means a charge in 10h
Discharge current | 10% | [%/h] |  |  |  |  | Standard value by battery technology (from MARGE):
Number of cycles | 1500 | [-] | [5 empty] | DOD max | Charging Rate max | Charging Rate recommanded | number of cycles, at the recommended DOD (25°C)
Round trip efficiency | 85% | [%] | - |  |  |  | Lead Acid Gel/VRLA | 50% | 20% | 10% | 1500
Number of cycles per year | 357 | [cycles] | Default 150 for grid connected system, 365 otherwise |  |  |  | Lead Acid OPZV/S | 50% | 20% | 10% | 3000
[7 empty] | Lithium ion | 80% | 100% | 50% | 6000
Battery properties |  |  | Comments: |  |  |  | Sodium | 80% | 20% | 20% | 4500
Voltage | 12 | [Volt] | Rated battery voltage
Battery type | Lead Acid Gel/VRLA | [-] | Type of battery |  |  |  | Good practices on battery voltage system (from MARGE):
Capacity | 200 | [Amper-hours] | Capacity of battery |  |  |  | PV size [Wp] |  | Voltage system
Advised (dis)-charge time | 10 | hours |  |  |  |  | min | max | [V] | [5 empty] | Source : https://www.researchgate.net/publication/333988217/figure/fig3/AS:773483957063680@1561424354034/The-number-of-cycles-of-the-battery-versus-the-depth-of-discharge-DOD-DOD-1-state.png
Power charge (advised) | 260.3165 | [Watt] | Power to charge battery in 5 hours |  |  |  | 0 | 250 | 12 |  |  |  | Default Voltage value for different technologies:
Power discharge (1CA) | 221.2691 | [Watt] | Power to discharge battery in 5 hours |  |  |  | 250 | 2500 | 24 |  |  |  |  | Charging voltage & current stages:
Surge (max 5s) | 442.5381 | [Watt] | Maximum Surge power output |  |  |  | 2500 | 15000 | 48
Cycles (50% DoD) | 1500 | [cycles] | Number of cycles (see 3rd image) | [5 empty] | Higher than 48V is not recommended
Comment | 0
Result |  |  | Comments:
Number of battery (power based) | 8.5647 | Items | Number of batteries required to deliver a power high enough for the demand
Number of battery (energy based) | 14.78 | Items | Number of batteries to have enough energy to supply hours of autonomy
Voltage advised | 48 | Volts | Voltage advised based on the system power
Number of years of use | 4.2017 | Years | Number of years where the system can be used at 25°C. This number can be halved if temperature is higher.
[13 empty] | Source : PV MINI-GRID INSTALLATION Dos & Don’ts | Source: https://www.dolphin-charger.com/media/global/news/bulletins/current-vs-voltage.jpg
Database Batteries |  |  |  |  | Database available in tool System Advisory Model 2021.12.2 https://sam.nrel.gov/
| Manufacturer | Model | Type | V | Ah | V_min | V_max | V_float | Capacity [hours] | Surge current | Cycles at 50 DoD | Datasheet | Comment
Vision CG12-200XA | Vision | CG12-200XA | Lead Acid Gel/VRLA | 12 | 200 | 11.6 | 12.8 | 12.4 | 10 | 1000 | 600 | CG12-200XA | No confident on the data
Victron GEL 24 OPzV 3000 turbular plate 2V cells battery | Victron | GEL 24 OPzV 3000 turbular plate 2V cells battery | Lead Acid OPZV/S | 2 | 1000 | [5 empty] | 2500 | https://www.europe-solarstore.com/victron-gel-24-opzv-3000-turbular-plate-2v-cells-battery.html
Rita DG12-200 | Rita | DG12-200 | Lead Acid Gel/VRLA | 12 | 200 | 11.58 | 12.9 | 13.7 | 10 | 300 | 1400 | https://www.ritarpower.com/uploads/ueditor/spec/DG12-200.pdf
Note on A10: Gauthier Limpens: Can be slightly higher than charge, but recommended to keep more or less the same

## 2bis. Hyb. Inverter
Hybrid inverter (advanced)
Input |  |  | Comments:
Demand nominal power | 2184 | [Watt] | Average power to be supplied
Demand surge power | 2184 | [Watt] | Peak power to be supplied
Security coefficient | 1.1 | [-] | Security to avoid over-tension/current. 1.25 is advised. Source : Do & Don'ts
Hybird inverter properties |  |  |  | Comments:
OUTPUT | Output power | 5500 | [Watt] | Nominal power that inverter can supply to load
| Output surge power | 11000 | [Watt] | Surge power that inverter can supply to load
INPUT | Input Power | 6000 | [Watt] | Maximal power that inverter can accepte by PV |  |  |  | Input DC
PV | V_PV max | 500 | [Volt] | Max acceptable voltage from DC PV
| V_PV min | 120 | [Volt] | Min acceptable voltage from DC PV
| V_PV start | 120 | [Volt] | Min voltage to start the controller
| I_PV max | 100 | [Amp] | Max acceptable current from DC PV
Battery | Voltage | 48 | [Volt] | Recommanded voltage system for batteries
| I_max | 100 | [Amp] | Max acceptable current from DC batteries
| Comment | 0
Result |  |  | Comments:
Number of inverter Output power | 1 | Items | Number of inverter required to supply teh AC demand
Number of inverter PV condition | 3 | Items | Number of inverter required to support the PV power input
Number of inverter final choice | 3 | Items | Max of the two previous constraints
Database hybrid inverters |  |  |  |  | Database available in tool System Advisory Model 2021.12.2 https://sam.nrel.gov/
|  |  | Output |  | Controller & Solar | [5 empty] | Batt |  |  | Other
| Manufacturer | Model | Rated output | Surge output | Type | Max P_dc_in | V_PV max | V_PV min | V_PV start | I_PV max | Voltage | V_charge | I_max | Datasheet | Comment
Solaredge SE3000H | Solaredge | SE3000H | 3000 |  |  | 4650 | 480 |  | 100 | 9 | 24 | 27 | 60 | SE3000H_ | "Missing information in datasheet: No clear data on Solar input constraints (V_PV start), no surge power"
Alpha Outback Energy SPC III 3000-24 | Alpha Outback Energy | SPC III 3000-24 | 3000 | 6000 | MPPT | 2000 | 380 |  | 120 | 60 | 24 |  | 60 | Alpha_OutBack_SPC_III | "Missing information in datasheet: - No current for battery indicated. - No minimal voltage for PV input minimum"
Raggie RG-MH5500W Plus | Raggie | RG-MH5500W Plus | 5500 | 11000 | MPPT | 6000 | 500 | 120 | 120 | 100 | 48 | 54 | 100

## 3. Design performances
Performances of the design:
Load
Load nominal | 2730 | [W]
Load max | 2730 | [W]
Load averaged | 2217 | [W]
Battery
Lifetime | 4.2017 | years | At 25°C, if temperature is higher, the performance might be drastically reduced.
Autonomy | 8.6604 | hours | With a nominal load
PV

## 3. BoQ
Department: '8/8
Item | Description | Unit | Qty | Rate (EUR) | Amount (EUR) | Comments
A | Solar system All cables to be Ultra-violet resistant. Solar panels will be mounted on a roof/stand-alone steel structure to be provided by Supplier |  |  |  |  | Choose if the system must be installed on a roof or stand alone. We advise roof when it is for a buildingµ
A.1 | 486W solar panel such as risen RSM150-8-485M. (see tech specs) | pcs | 12 | 200 | 2400
A.2 | PV Solar cable 4mm² with the MC4-male and femal connectors propely crimped. Cable used to connect PV pannels in serie | m | 24 | 6 | 144
| PV Solar cable 6mm² with the MC4-male and femal connectors propely crimped. Cable used to connect PV pannels in parallel up to the junction box | m | 60 | 6 | 360
A.3 | Lightning protection HO5 V/K copper cable (flexible) single-pole / minimum section 16mm² ; should be compliant with NFC 32-201 standard and installed according to UTE C15-712-1 guide | m | 28 | 3 | 84
A.4 | Junction Box installed near the panels. It collect the parallel circuits and send the power to the controller. (see tech specs) | pcs | 3 | 130 | 390
A.6 | Cable 3G6mm² from the junction box and inverter | m | 90 | 6 | 540
A.7 | Supply and install Lightning Surge Protection Device (type II or type B) on the 2 phases between Solar panels and controller and between Umeme connection and Power adaptor. Provide 1 spare lightning arrester cartridges | pcs | 4 | 75 | 300
A.8.4 | Supply and install an hybrid inverter with in-built controller of AC output power of 5.5 kW or more, such as Raggie RG-MH5500W Plus or equally approved. See tabular technical specifications for the ones inverter must respect. | pcs | 3 | 2174 | 6522
A.9 | 12V, 200Ah, lifetime of 1500 cycles at 50% depth of Discharge at 25°C. Such as Rita DG12-200 | pcs | 16 | 408 | 6528
A.10 | DC breaker for battery system or equivalent fuse. Lifetime of at least 25 years. If fuse is procured, provide 1 spare catridge). | pcs | 3 | 35 | 105
A.11 | Lockable steel battery cabinet of dimensions 1500 x 600 x 500 mm to store 8 batteries, covered with 1.2 mm mild steel plates on all side with air vents and lockable door at the front. | pcs | 2 | 150 | 300
A.12 | Battery cable of 16mm² or above connected between the inverter and the battery bank. | m | 30 | 6 | 180
| Busbar for connections of batteries in parallel, adapted for the battery system. | pcs | 2 | 30 | 60
A.13 | Low Voltage Switchboard containing AC input for inverter and AC output from inverter to load. (see tech specs) | pcs | 3 | 130 | 390
A.14 | Installation costs | pcs | 1 | 400 | 400
| Sub_Total |  |  |  | 18703
B | Visual information & knowledge management The following items will be supplied and/installed for the purpose of Maintenance and Operations of the installed systems
B.1 | Operational manual; Comprehensive Operation and Maintenance manual for the installed system, written in English and graphically illustrated for unambiguous interpretation and understanding by Operation and Maintenance staff. Special attention shall be drawn to fault finding and remedial action. The manual shall include a system wiring diagram, a list of spare parts and the names of the accredited suppliers/agents of these spare parts. The manual shall also include the manufacturer's name, model number, service manuals, parts list and brief descriptions of all equipment and their basic operating features i.e. routine maintenance procedures, possible breakdowns and repairs, recommended spare parts, troubleshooting guide, equipment layout and simplified wiring and control diagrams of the system as installed. | pcs | 1 | 35 | 35
B.2 | Component signage; each component of the installed systems should be clearly labelled onto sticker paper or equal/better approved material and securely mounted directly adjacent to the component. The lettering shall be high contrast and no less than 50mm and no more than 75mm in size. Sites where only specific components are being replaced will be treated similarly to sites where full installations will be done; i.e. labels will also be installed against all existing components of systems where the contractor only replaces certain parts. | Ls | 1 | 10 | 10
B.3 | System chart (electrical layout); an A1 size chart showing the entire system with its parts and wiring, labelled in English, securely mounted at a location readily accessible and easily understood by Operation and Maintenance staff. The lettering and drawings will be high contrast for good visibility. | pcs | 1 | 35 | 35
B.4 | Error/warning chart; an A1 size chart illustrating common warning signs and error messages, and their meanings, labelled in English, securely mounted at a location readily accessible and easily understood by Operation and Maintenance staff. The lettering and drawings will be high contrast for good visibility. | pcs | 1 | 35 | 35
| Sub_Total |  |  |  | 115
D | Lightning All materials to be supplied and installed to obtain at most 10ohms earth resistance in both improved cases and new cases.All termination points to be properly done.
D.1 | 16mm(D)*1000mm(L) air terminal | pcs | 2 | 41 | 82
D.2 | HO5 V/K copper cable (flexible) single-pole / minimum cross-section 16mm2 for all equipotential connections and earthing; Compliant with the NFC 21-201 standard | pcs | 1 | 3 | 3
D.3 | 3mm*25mm copper tape hard drawn complete with sadles. | m | 25 | 13 | 325
D.4 | 20mm(D)*1200mm(L) earth conductor of hard drawn copper complete with connection clamp and driving tip | pcs | 1 | 72 | 72
D.5 | Inspection Manhall of diameter 300mmx300mm | pcs | 1 | 43 | 43
D.6 | Earthing: excavate pit 1500 x 1200 x 1500 mm (L x W x D) and place course salt mixed with charcoal dust and soil in pit and compact and drive electrodes into this pit, connect and place precast manhole 300 x 300 x 300 mm complete with cover marked with earth symbol and connect up ready and measure the resistance. | pcs | 1 | 9 | 9
D.7 | Rod to tape connector | pcs | 4 | 35 | 140
D.8 | Installation costs | Ls | 1 | 43 | 43
| Sub_Total |  |  |  | 717
E | Adaptation of electrical system of the building for solar system. This includes the adaptation of existing board, installation of new wires and sockets.
E.1 | Adaptation of switches and ligths. New wiring should be 3G1.5mm² or more. | pcs | 14 | 16 | 224
E.2 | New sockets and wiring 3G2.5mm² XVB (or equivalent) up to the solar board. | pcs | 10 | 19 | 190
E.3 | Electrical layout plan of the building & single phase diagram | pcs | 1 | 87 | 87
| Sub_Total |  |  |  | 501
| Grand Total(Vat Exclusive) |  |  |  | 20036

## 3. BoQ_tech_specs
Component | Technical specifications to respect:
PV panels | Lifetime of at least 25 years
Conform to CEI 61215 et CEI 61730-1-2
Warranty of min 90% of power after 10 years and 80% at 25 years
Aluminium frame
Provided wired with junction box with at least 3 by-pass diodes, with connectors PV type MC4 and wire at least 4mm²
Solar wire | Lifetime of at least 25 years
Wire of 4 mm² section on the pannels in serie and at least 6mm² for the rest. They should be with connectors of type MC4
Conform to UTE C32-502
Junction box | Lifetime of at least 15 years
Put as close as possible to the Pannels
Accessible to a technician from outside without need of tools.
At least IP44
Protection of mechanical chocks conform to the norm IK07 according to NF EN 62262 norm
Conception should be in line with UTE 15-712-1 (July 2013).
Disconnecting switches: disconnecting the entire PV array
Implementation of surge protectors downstream of the disconnecting switches; It should be of type 2 (or type B) conform to the norm NF EN 50539-11
Spare lightning arrestor cartridges (01 unit per box).
Grouding of panels and its structure | - Lifetime 25 years
- Connected to the earth distributor and up to the earth rod ;
- HO5 V/K copper cable (flexible) single-pole / minimum cross-section 16mm2 for all equipotential connections and earthing;
- Compliant with the NFC 32-201 standard.
Surge protector (ligthning) earthing | - Lifetime 25 years
- Connected to the main equipotential cable
- HO5 V/K copper cable (flexible) single-pole / minimum section 16mm2 ;
- Compliant with the NFC 32-201 standard;
- Compliance with the installation distances as specified in the UTE C15-712-1 guide
Ground stakes | - Life span 25 years
- Minimum size: 01 metre ;
- Copper plated steel with its connecting lug (for bare copper cable from 16 to 70mm²);
- 16mm diameter, 254 micron copper plating;
- Supplied with a copper earthing strip, to isolate the earth network when measuring earth.
Inverter (hybrid or not) | - Lifetime 10 years
- Available power from -25°C to 60°C ;
- Rated power (KVA) greater than or equal to 95% of the peak power (kWp) connected to the inverter;
- MPPT tracker controllers in-built;
- Maximum efficiency > 90 % ;
- Efficiency at 10% PNOM > 85%;
- Internal short circuit protection on AC output;
- In-built surge protection
- Reverse polarity protection;
- Overload protection;
- Display and function button accessible for operation of various inverter functions;
- Minimum protection class I ;
- Low self-consumption
- SCADA status and error visualisation tools Available via SD card and remote tool
- Minimum 5 year manufacturer's warranty
- Charging algorithm adapted to the battery technology, compatible with lithium batteries;
- Output voltage 230V pure sine (TDH < 3%), 50Hz ;
- Voltage thresholds for different charging modes (absorption, equalisation, boost), alarms and low battery protection, with adjustable voltage threshold, period and duration
Low Voltage Switchboard | - Lifetime 25 years except for the active components and protection components;
- the AC input (from utility or generator) should be protected by a surge protector.
- The AC board will group together all the AC outputs of the inverters and the power supply outlets of the buildings through the AC busbar;
- PVC enclosure or IP54 metal cabinet;
- Wall mounting ;
- Cable gland for flexible cable at the bottom of the enclosure;
- Rated current of the circuit breakers > or = 1.4 times the maximum transit current in the associated rated regime;
- Protection of the cables by thermal-magnetic circuit breakers curve C or fuses;
- AC lightning protection type II (or type B);
- Spare lightning arrester cartridges (01 unit per cabinet).
Batteries specifications | Lifetime of 1500 cycles at 50% depth of Discharge and ambiant tempearture.
Capacity, brand and manufactured year should be clearly visible on each battery
Procured with datasheet and user manual.
Connection of batteries | Lifetime of 25 years
DC connector with box